## Sheet1
Sampling Date | 2017-07-20 | 2016-07-20 | Oil Volume | 10000 | litres
Hydrogen | 500 | 100 | Has OLTC | FALSE
Methane | 200 | 20
Ethane | 5 | 2.5
Ethylene | 10 | 5
Acetylene | 2000 | 2
Carbon Monoxide | 4000 | 50
Carbon Dioxide | 9000 | 500
Oxygen | 4994 | 4994
Nitrogen | 30933 | 30933
Serialised DGA Data | {"SamplingDate":"2017-07-20T00:00:00","Hydrogen":{"Value":500.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Methane":{"Value":200.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Ethane":{"Value":5.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Ethylene":{"Value":10.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Acetylene":{"Value":2000.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"CarbonMonoxide":{"Value":4000.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"CarbonDioxide":{"Value":9000.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Oxygen":{"Value":4994.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Nitrogen":{"Value":30933.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}}}
{"SamplingDate":"2016-07-20T00:00:00","Hydrogen":{"Value":100.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Methane":{"Value":20.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Ethane":{"Value":2.5,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Ethylene":{"Value":5.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Acetylene":{"Value":2.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"CarbonMonoxide":{"Value":50.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"CarbonDioxide":{"Value":500.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Oxygen":{"Value":4994.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}},"Nitrogen":{"Value":30933.0,"Unit":{"Name":"Parts per Million","Symbol":"PPM","Base":1.0,"Family":"Concentration"}}}
IEC 60599 | [ Title => Interpretation of Dissolved Gas Analysis as per IEC60599 Edition 3.0, 2015-09 ] [ CO2 / C0 => The Carbon Dioxide to Carbon Monoxide Ratio (CO2/CO) is 2.25 which is less than 3. This is generally considered as an indication of probable paper involvement in a fault, with possible carbonization, in the presence of other fault gases. ] [ O2 / N2 => Dissolved O2 and N2 are found in oil as a result of contact with atmospheric air in the conservator of air-breathing equipment, or through leaks in sealed equipment. At equilibrium with air, the concentrations of O2 and N2 are approximately 32000 and 64000 ppm respectively and the O2/N2 ratio is approx. 0.5. In service, this ratio may decrease as a result of oil oxidation and/or paper ageing, if O2 is consumed more rapidrly than it is repalce by difussion. Factors such as the load and preservation system used may also affect the ratio, but with the exception of closed systems, ratios less than 0.3 (0.16 in this case) are generally considered to indicate excessive consumption of oxygen. ] [ C2H2 / H2 => Although this transformer has been identified as not having communication between the On-Load Tap Changer oil and the main tank oil, Acetylene to Hydrogen ratios higher than 2 or 3 in the main tank (4.00 in this case) are considered as an indication of OLTC contamination. This can be confirmed by comparing DGA results in the main tank, in the OLTC and in the conservators. ] [ Hydrogen Rate of Change => The rate of change of Hydrogen is 4000000.00 ul/year which is higher than the typical value of 1320000.00 ul/year. ] [ Methane Rate of Change => The rate of change of Methane is 1800000.00 ul/year which is higher than the typical value of 1200000.00 ul/year. ] [ Ethane Rate of Change => The rate of change of Ethane is 25000 ul/year which is lower than the typical value of 50000 ul/year. ] [ Ethylene Rate of Change => The rate of change of Ethylene is 50000 ul/year which is lower than the typical value of 320000 ul/year. ] [ Acetylene Rate of Change => The rate of change of Acetylene is 19980000.00 ul/year which is higher than the typical value of 370000.00 ul/year. ] [ CarbonMonoxide Rate of Change => The rate of change of CarbonMonoxide is 39500000.00 ul/year which is higher than the typical value of 10600000.00 ul/year. ] [ RateOfChangeExceeded => True ] [ Hydrogen Concentration => The concentration of Hydrogen is 500.00 ul/l which is higher than the typical value of 150.00 ul/l. ] [ Methane Concentration => The concentration of Methane is 200.00 ul/l which is higher than the typical value of 130.00 ul/l. ] [ Acetylene Concentration => The concentration of Acetylene is 2000.00 ul/l which is higher than the typical value of 280.00 ul/l. ] [ CarbonMonoxide Concentration => The concentration of CarbonMonoxide is 4000.00 ul/l which is higher than the typical value of 600.00 ul/l. ] [ LimitExceeded => True ] [ Final Diagnosis => Alarm ]